Release Notes: ECX-AC6000

Firmware Package: 2021.02.24

This document outlines the release notes for the ECX-AC6000 firmware package dated 2021.02.24 (YYYY.MM.DD). The package file is named “AC6000\_2021.02.24\_Release.zip”. This firmware package officially brands the UPS as an Enconnex product and provides stability, performance, and diagnostic enhancements.

* Addresses issues related to the 305 inductor over current fault
* Fixed front panel menu issue where IPv4 DHCP enable/disable setting was inaccessible
* Fixed text issue on front panel display causing character errors when a value exceeds 4 digits in the UPS menu

This firmware package contains the following versions for each respective controller as viewed through the local web page or the AC6000 Reflash software:

|  |  |
| --- | --- |
| **Controller** | **Version** |
| UI | 1.8.7 |
| FPC | 1.9.1 |
| System Control | 1.7.6 |
| Boost | 1.3.2 |
| BMS Control | 3.0.5 |
| BMS Monitors 1-4 | 2.1.4 |
| Mpfs (local web page) | 1.8.3 |
| AC6000 Reflash Software | 1.0.7 |